Automation & Operational Technology – MDF Work Package

### Document Control

| Version No. for Final Release | V1.0 |
| --- | --- |
| Issue Date | 01/2/2026 |
| Status: Draft or Final | review |
| Document Owner |  |
| Audience |  |
| Approval for Final Release |  |

### Project Overview / Warehouse Details

- Project Name: [Project Name]

- FBM ID: [FBM ID]

- Site address: [Site Address]

- SITE ID: [Site ID]

- Dates:

Date – Access to Site

Date – Start of MDF Deployment

Date – Finalization of MDF Deployment Date – Go live

- Site layout / Diagram Floor and Office (see Appendix 1)

- MDF Location (see Appendix 2)

# 2 Scope of Work (SoW)

The Main Distribution Frame (MDF) serves as the central termination point for all network infrastructure within the facility. This document outlines the scope of work for the design, installation, and configuration of the MDF including network switches, power distribution, cooling, cable management, and associated equipment.  
Design, delivery, and implementation of the MDF network infrastructure, including:

### MDF Infrastructure

- Network design: topology, IP schema, routing, redundancy, and segmentation

- Hardware/software supply: core/distribution switches, patch panels, UPS, PDUs, cable management

- Professional services: site survey, rack installation, cabling, configuration, testing, and commissioning

- 24×7 support: NOC monitoring, maintenance, and escalation handling

### Physical Scope Summary

- Number of Users Supported: [TBD – to be confirmed based on site headcount]

- Operation Hours: [TBD – confirm with total number of shifts]

- Number of IDF Locations: [TBD – confirm total IDF count connected to this MDF]

- Number of MDF Racks: [TBD – 1 / 2 / 3 rack configuration]

- Estimated Cable Runs: [TBD – based on IDF distances and floor layout]

- Network Segments: Data, Voice, WLAN (colour-coded per segment)

### Security & Compliance

- Access control: electronic badge entry with full audit logs on MDF room

- Fire suppression and environmental monitoring integrated to NOC/BMS

# 3	Functional Requirements

- MDF room must provide adequate physical security with lockable access control.

- Environmental conditions must be maintained within operational specifications:

  - Temperature: 18°C to 27°C (64°F to 81°F)

  - Humidity: 20% to 80% non-condensing

- Fire suppression systems must comply with local building codes and data centre standards.

- All equipment must be properly grounded to prevent EMI and ensure electrical safety.

- Cable management systems must be implemented to maintain organization and prevent damage.

- Clear labelling and documentation must be maintained for all equipment, connections, and cable runs.

- Adequate ventilation and cooling must be provided to prevent equipment overheating.

- Power redundancy must be implemented where critical systems are deployed.

- All installations must comply with ANSI/TIA-568, ANSI/TIA-569, and ISO/IEC 11801 standards.

# 4	Technical Requirements

## 4.1	Rack Infrastructure

- Industrial-grade server racks with lockable doors and ventilation panels.

- Rack size: [TBD] U (standard 42U or as per design).

- Rack mounting: Floor-standing with seismic anchoring where required.

- Minimum rack depth: 800mm to accommodate deep switches and patch panels.

- Cable management: Vertical and horizontal cable managers with finger ducts.

- Rack must support distributed load of [TBD]kg.

## 4.2	 Network Switches Installation

- Core and distribution layer switches to be rack mounted.

- All switches must place as per Network design and labelled.

- Cables connected to Switch uplink is to be labelled as per design documentation.

## 4.3	Uninterruptible Power Supply (UPS)

- UPS must provide backup power to critical network equipment.

- Capacity: [TBD] kVA or as per load calculation.

- Runtime: Minimum [15/30] minutes at full load to allow graceful shutdown.

- UPS must include battery monitoring and management capabilities.

- Integration with building management system (BMS) or SNMP monitoring where applicable.

- Rack-mounted or floor-standing UPS based on capacity requirements.

## 4.4	Power Distribution Units (PDU)

- Rack-mounted PDUs with adequate outlet capacity.

- Minimum outlets per rack: [8/12/16] based on equipment density.

- Support for both standard and high-amperage devices.

- PDUs must include surge protection and circuit breakers.

- Intelligent PDUs with remote monitoring preferred for critical deployments.

## 4.5	Cooling and Grounding

- Adequate HVAC system to maintain temperature and humidity within specified ranges.

- Rack-mounted cooling fans or dedicated cooling units are recommended for large installations

- Hot aisle / cold aisle configuration recommended for larger installations.

- Temperature monitoring sensors to alert on threshold breaches.

- All racks and metal enclosures must be properly grounded.

- Grounding must comply with ANSI/TIA-607 and local electrical codes.

## 4.6        Doors

- Fire‑rated door (minimum 1‑hour rating), solid-core metal construction.

- Self‑closing, self‑latching; no windows unless fire‑rated.

- Electronic badge access with full entry/exit audit logs.

- Fail‑secure lock and door position sensor tied to security system.

- Fully sealed door to support clean‑agent room integrity (no gaps, no cable penetrations).

- No penetrations through the door or frame—cables must route through sealed conduits in walls.

- Exterior signage: “MDF – Authorized Personnel Only.”

## 4.7      Fire Suppression

- Clean-agent system (FM‑200 or Novec 1230); electronics‑safe, no residue.

- Early-warning smoke detection (preferred: VESDA) integrated with building fire alarm.

- Cross‑zone detection required before discharge; includes manual pull and abort switch outside the room.

- Automatic HVAC shutdown on activation to maintain gas concentration.

- Room integrity sealing (all penetrations sealed; must pass door fan test).

- Self-contained control panel with UPS/battery backup for minimum required runtime.

- Monitoring signals (alarm, trouble, low pressure) integrated to NOC/BMS.

- Environmental monitoring for temperature and humidity (ASHRAE TC 9.9 compliant).

- Clear signage outside: “Clean Agent Protected Area – Do Not Enter During Alarm.”

## 4.8    Room Size & Construction

These sizes include rack footprint, service clearance, HVAC space, fire suppression equipment, cable trays, door swing, and safety access.

- 1 Rack MDF (8–10 m²)

  - 1 × 42U rack with 1–1.5 m front aisle and 0.9–1 m rear clearance.

  - Includes wall space for UPS, sensors, cable trays, and fire system.

- 2 Rack MDF (12–15 m²)

  - Two racks in a row with 1.2–1.5 m front aisle and 1 m rear clearance.

  - Space for power panel, fire panel, sensors, and cable routing.

- 3 Rack MDF (16–20 m²)

  - Three racks with 1.2–1.5 m front aisle and ≥1 m rear aisle.

  - Room zones for HVAC, UPS, fire suppression, and BMS integration

- Sealed walls, floor, and ceiling with anti-dust coating.

- Cable trays/ladder racks and fire-rated wall penetrations

# 5	Deliverables

## 5.1 MS1.3 – Provision of Design & Procurement

Procurement, design and delivery of all equipment as defined in Sections 1–3

Physical installation of equipment in designated locations

Installation of accessories and peripherals as required

## 5.2 MS2 – FAT (Factory Acceptance Testing)

Factory acceptance testing and verification of all hardware prior to site delivery

Pre-staging and configuration of equipment as per technical requirements

Confirmation of full Bill of Materials receipt and manufacturer warranty coverage

## 5.3 MS3 – SAT (Site Acceptance Testing & Commissioning)

Physical installation and commissioning of all equipment on site

Connectivity and integration testing (network, power, and application layer)

Validation that all delivered equipment meets Section 3 requirements

All equipment must be validated and ready for operational use prior to Go-Live

## 5.4 MS4 – UAT (User Acceptance Testing)

Operations user acceptance testing

Asset inventory including: Device type, Model, Serial number

Mapping of devices to: Users, Stations, Rooms or operational areas

Handover of equipment to site management and operations team

Provision of support and escalation contacts

## 5.5 MS5 – Hypercare & Project Closure

Hypercare support during initial operational period

Confirm NOC monitoring and SLA reports (where applicable)

Validate all documentation required for handover to support is complete

Final project acceptance sign-off and closure

| Milestone | Activity / Deliverable |
| --- | --- |
| MS0 – Kick-Off | Internal Kick-Off Meeting |
| MS1.1 – Provision of Requirements | - Infrastructure (WAN/LAN/WLAN/Perimeter): MDF Room Layout requirements. - Rack elevation diagrams showing equipment placement - Cooling and ventilation design specifications - As-Built Drawings |
| MS1.2 – Provision of Suppliers | - Infrastructure: List down MDF/IDF specific hardware from Network BoM - Complete list of racks, switches, patch panels, UPS, PDUs, cables, and accessories. Include manufacturer, model, and compliance certifications |
| MS1.3 – Provision of Designs | - Procurement: Quote and PO for AOT Hardware - Procurement: Quote and PO for Network Hardware/Cabling |
| MS2 – FAT (Factory Acceptance) | - Full BOM received- Confirmation of all Hardware devices received and Factory acceptance testing complete. Confirm Manufacturer warranty for equipment and components. |
| MS3 – SAT (Unit Testing & Commissioning) | - Network Cabling Installation - Prestaging and Commissioning of MDF applicable devices - MDF hardware installation and configuration - Network Testing |
| MS4 – UAT (Integration & User Acceptance) | - OPS User Acceptance Testing |
| MS5 – Hypercare | - Validate all documentation required for hand-over to support is ready - Hypercare Support: Manage expectations for troubleshooting |

| Standard | Scope |
| --- | --- |
| ANSI/TIA-568 | Cabling infrastructure and performance |
| ANSI/TIA-569 | Pathways and spaces for telecommunications |
| ANSI/TIA-607 | Grounding and bonding |
| ISO/IEC 11801 | Generic cabling for customer premises |
| ASHRAE TC 9.9 | Environmental monitoring (temperature/humidity) |
| Local Building Codes | Fire suppression, door ratings, and electrical safety |
| UL / Equivalent | Equipment and component certification |

# 8	Appendix 2 – MDF Room Layout

Detailed MDF room layout showing rack placement, power distribution, cooling units, and cable pathways.

# 9	Appendix 3 – Rack Elevation Diagram

Rack elevation diagrams showing equipment placement, U-space allocation, and cable management.

# 10	Appendix 4 – Network Topology

Network topology diagram showing MDF as central point with connections to IDFs, endpoints, and external circuits.