Automation & Operational Technology – MDF Work Package

### Document Control

| Version No. for Final Release | V1.0 |
| --- | --- |
| Issue Date | 01/2/2026 |
| Status: Draft or Final | review |
| Document Owner |  |
| Audience | xxxxxxx |
| Approval for Final Release |  |

### Project Overview / Warehouse Details

Project Name:

FBM ID:

Site address:

SITE ID:

Dates:

MS1.1 – Provision of Supplier - xx/xx/2026

MS1.2 – Provision of Design - xx/xx/2026

MS2 – Factory Acceptance / Lab Testing / Simulation - xx/xx/2026

MS3 – Unit Testing - xx/xx/2026

MS4.1 – Site Integration - xx/xx/2026

MS4.2 – UAT (User Acceptance Testing) - xx/xx/2026

MS5 – Hypercare - xx/xx/2026

MS6 – Business as Usual Support - xx/xx/2026

# 1. Scope of Work (SoW)

The Main Distribution Frame (MDF) serves as the central termination point for all network infrastructure within the facility. This document outlines the scope of work for the design, installation, and configuration of the MDF including network switches, power distribution, cooling, cable management, and associated equipment.  
Design, delivery, and implementation of the MDF network infrastructure, including:

### MDF Infrastructure

- Network design: topology, IP schema, routing, redundancy, and segmentation

- Hardware/software supply: core/distribution switches, patch panels, UPS, PDUs, cable management

- Professional services: site survey, rack installation, cabling, configuration, testing, and commissioning

- 24×7 support: NOC monitoring, maintenance, and escalation handling

### Physical Scope Summary

- Number of Users Supported: [TBD – to be confirmed based on site headcount]

- Operation Hours: [TBD – confirm with total number of shifts]

- Number of IDF Locations: [TBD – confirm total IDF count connected to this MDF]

- Number of MDF Racks: [TBD – 1 / 2 / 3 rack configuration]

- Estimated Cable Runs: [TBD – based on IDF distances and floor layout]

- Network Segments: Data, Voice, WLAN (colour-coded per segment)

### Security & Compliance

- Access control: electronic badge entry with full audit logs on MDF room

- Fire suppression and environmental monitoring integrated to NOC/BMS

# 2. Functional Requirements

- MDF room must provide adequate physical security with lockable access control.

- Environmental conditions must be maintained within operational specifications:

  - Temperature: 18°C to 27°C (64°F to 81°F)

  - Humidity: 20% to 80% non-condensing

- Fire suppression systems must comply with local building codes and data centre standards.

- All equipment must be properly grounded to prevent EMI and ensure electrical safety.

- Cable management systems must be implemented to maintain organization and prevent damage.

- Clear labelling and documentation must be maintained for all equipment, connections, and cable runs.

- Adequate ventilation and cooling must be provided to prevent equipment overheating.

- Power redundancy must be implemented where critical systems are deployed.

- All installations must comply with ANSI/TIA-568, ANSI/TIA-569, and ISO/IEC 11801 standards.

# 3. Technical Requirements

## 3.1	Rack Infrastructure

- Industrial-grade server racks with lockable doors and ventilation panels.

- Rack size: [TBD] U (standard 42U or as per design).

- Rack mounting: Floor-standing with seismic anchoring where required.

- Minimum rack depth: 800mm to accommodate deep switches and patch panels.

- Cable management: Vertical and horizontal cable managers with finger ducts.

- Rack must support distributed load of [TBD]kg.

## 3.2	 Network Switches Installation

- Core and distribution layer switches to be rack mounted.

- All switches must place as per Network design and labelled.

- Cables connected to Switch uplink is to be labelled as per design documentation.

## 3.3	Uninterruptible Power Supply (UPS)

- UPS must provide backup power to critical network equipment.

- Capacity: [TBD] kVA or as per load calculation.

- Runtime: Minimum [15/30] minutes at full load to allow graceful shutdown.

- UPS must include battery monitoring and management capabilities.

- Integration with building management system (BMS) or SNMP monitoring where applicable.

- Rack-mounted or floor-standing UPS based on capacity requirements.

## 3.4    Room Size & Construction

These sizes include rack footprint, service clearance, HVAC space, fire suppression equipment, cable trays, door swing, and safety access.

- 1 Rack MDF (8–10 m²)

  - 1 × 42U rack with 1–1.5 m front aisle and 0.9–1 m rear clearance.

  - Includes wall space for UPS, sensors, cable trays, and fire system.

- 2 Rack MDF (12–15 m²)

  - Two racks in a row with 1.2–1.5 m front aisle and 1 m rear clearance.

  - Space for power panel, fire panel, sensors, and cable routing.

- 3 Rack MDF (16–20 m²)

  - Three racks with 1.2–1.5 m front aisle and ≥1 m rear aisle.

  - Room zones for HVAC, UPS, fire suppression, and BMS integration

- Sealed walls, floor, and ceiling with anti-dust coating.

- Cable trays/ladder racks and fire-rated wall penetrations

## 3.5    Compliance & Standards

- All MDF installations must comply with the following standards:

| Standard | Scope |
| --- | --- |
| ANSI/TIA-568 | Cabling infrastructure and performance |
| ANSI/TIA-569 | Pathways and spaces for telecommunications |
| ANSI/TIA-607 | Grounding and bonding |
| ISO/IEC 11801 | Generic cabling for customer premises |
| ASHRAE TC 9.9 | Environmental monitoring (temperature/humidity) |
| Local Building Codes | Fire suppression, door ratings, and electrical safety |
| UL / Equivalent | Equipment and component certification |

# 4. Deliverables

Planning

MS1.1 – Provision of Supplier – delivery date

- Full Bill of Materials (BoM) submitted and validated, including manufacturer, model, part numbers, port/component specifications, and compliance certifications

- Approved Purchase Orders confirmed for all equipment and professional services

MS1.2 – Provision of Design - delivery date

- Design documentation issued: network topology, connectivity diagrams, rack elevation diagrams, floor plan layouts, IP schema, VLAN and segmentation design, and cable routing plans

- Procurement and delivery of all equipment as defined in Sections 1–3 initiated and tracked against BoM

Execute

MS2 – Factory Acceptance / Lab Testing / Simulation - delivery date

- Full BoM receipt confirmed; manufacturer warranty coverage verified for all equipment and components

- Pre-staging and configuration completed as per Section 3 technical requirements

- Factory acceptance testing executed and signed off prior to site delivery

MS3 – Unit Testing - delivery date

- Physical installation and commissioning of all equipment on site, including accessories, peripherals, mounting hardware, and cabling

- As-built drawings and installation photos produced, reflecting final installed routes, placements, termination points, and labelling

- Certified test reports produced for all applicable runs and systems (e.g. Fluke cable certification, UPS runtime, RF coverage, VLAN and uplink validation)

- Compliance documentation confirmed against applicable standards (ANSI/TIA-568, ISO/IEC 11801, fire safety, and any OT-specific industrial standards)

MS4.1 – Site Integration - delivery date

- Connectivity and integration testing completed across network, power, and application layers

- Validation evidence confirms all delivered equipment meets Section 3 requirements; outstanding items logged in a punch list with agreed resolution dates

MS4.2 – UAT (User Acceptance Testing) - delivery date

- Operations UAT completed and signed off by site management

- Asset inventory compiled: device type, model, serial number, firmware version, and registered in snow CMDB

- Devices mapped to assigned users, workstations, rooms, or operational areas

- RF Guns/RDT devices registered in SOTI as a mandatory task

- All documentation delivered in soft copy formats

- Formal handover of equipment to site management, including credentials and escalation contacts

Go Live

MS5 – Hypercare - delivery date

- Hypercare support active during agreed initial operational period; incidents logged and resolved

- NOC monitoring confirmed active and initial SLA report issued (where applicable)

- All handover documentation validated as complete: as-built drawings, configuration backups, test reports, compliance records, asset register, and warranty certificates

MS6 – Business as Usual Support - delivery date

- Final project acceptance signed off; project formally closed

- Support transitioned to BAU team with full handover pack, escalation matrix, and SLA documentation in place

- All outstanding punch list items resolved or formally accepted and transitioned to BAU tracking

5. Appendix

5.1 Appendix 1 – Site Layout

Site layout diagram showing MDF location within facility.

# 5.2 Appendix 2 – MDF Room Layout

Detailed MDF room layout showing rack placement, power distribution, cooling units, and cable pathways.

# 5.3 Appendix 3 – Rack Elevation Diagram

Rack elevation diagrams showing equipment placement, U-space allocation, and cable management.

# 5.4 Appendix 4 – Network Topology

Network topology diagram showing MDF as central point with connections to IDFs, endpoints, and external circuits.